## Slide 1: Inspection & testing of electrical installations
Outcome 1

## Slide 2: Inspection & testing: What’s the difference?
Inspection
Electrical inspection requires a visual check of the apparatus. It is self-explanatory, you inspect the wiring, the enclosures like switchgear, conduit and trunking, terminations etc.​
The inspection is a two-stage process, the first stage is continuous throughout the life of the job you are doing. Every task you do or observe being done you should be constantly aware of the 4 main reasons of inspection.​
Undamaged equipment.​
The correct type of equipment for the installation.​
Proper positioning and fixing of equipment.​
Equipment is manufactured to a recognised standard.​
​

## Slide 3: Inspection & testing: What’s the difference?
Testing
The purpose of testing any electrical installation is to ensure that it meets the requirements of BS 7671.​
The requirements are that the installation should be safe to operate and should protect persons, property and livestock against dangers or damage that may occur when the electrical installation is in use.​
Dangerous situations are we trying to prevent happening by testing installations are​:
Electric Shock.​
Excessive temperature causing fire or burns​
Accidental mechanical movement​
Explosion​
Under Voltage​
Power Supply Interruption​
Arching​
​

## Slide 4: Inspection & testing: What’s the difference?
Testing
Situations where incorrect or no testing may cause the above effects to occur.​
​
Damaged Cables – Short circuit​
Wrong size or type of cables – Overload​
Wrong connections – Earth Fault​
Wrong size or type of protective device – Electric Shock ​
Reversed Polarity​
No continuity​
Incorrect operation
​

## Slide 5: Inspection & testing: What’s the difference?
Testing
Situations where incorrect or no testing may cause the above effects to occur.​
​
Damaged Cables – Short circuit​
Wrong size or type of cables – Overload​
Wrong connections – Earth Fault​
Wrong size or type of protective device – Electric Shock ​
Reversed Polarity​
No continuity​
Incorrect operation
​

## Slide 6: Ten Items/areas of inspection
​
Labels on equipment​
Bonding​
Cable/conductor sizes ​
Cable types​
Connections ​
BS/CE symbols​
Damaged equipment ​
Rating of equipment​
Suitability of accessories ​
Positioning of Equipment
​

## Slide 7: Common problems found during inspections!
​
Restricted access​
Damaged Cables​
Loose Connections​
Missing Labels​
No Circuit Identification charts or wrong info​
Circuit Protective devices wrong – size/type​
Wrongly positioned equipment​
Additional equipment fitted – not on diagram or schedule​
Bonding cables wrongly fitted or sized​
Enclosure capacities exceeded
Foreign Ingress
​

## Slide 8
Chaffing of insulation can leave live conductors exposed.
Electrical equipment deteriorates naturally with age. Insulation deterioration can occur in areas where excessive vibration and temperature occurs.
Therefore, increasing the risk short circuit faults.
Common problems: Damaged cable insulation

## Slide 9
If cables are damaged, then they should be replaced with the same approved type. Here is a poor attempt at insulation repair.
Common problems: Damaged cable insulation

## Slide 10
Moisture ingress inside electrical enclosures leads to rusting & corrosion.
Common problems: Moisture ingress

## Slide 11
Overheating in an electrical circuit could be due to loose connections.
Common problems: Loose connections

## Slide 12
Overload can result in overheating.
Common problems: Misuse of electrical equipment