## Slide 1: Outcome 2: Testing
Perform the tests required for a low voltage electrical installation prior to connection of the supply

## Slide 2: Testing
This outcome will look at the testing required on electrical circuits. The main focus will be on dometic wiring and installations. What we would typically find in a house. All test must be carried out with the circuit dead and safety isolated.
For the testing we are using a Insulation Resistance Tester: The test is carried out using a multi-function tester.
Note: The process for xero leads may differ if you are using a different tester- Refer to manual before use.

## Slide 3: Polarity Testing
Purpose​
Confirm that overcurrent devices and single pole controls are in the line conductor only​
Equipment ​-
IR tester/ Low ohm meter and Link Cable
Setting​
Lowest​/ usually Auto range
Measured in​
Ohms Ω - Null leads before test
Testing 1 way Light Switch

## Slide 4
1: Prior to testing ensure all loads are disconnected , breakers are off and secured.
2: Connect the leads to your meter, we need zero your leads. Switch meter to Ohms and connect a link
Cable between them.

## Slide 5
Step3: You will see a reading, this is the error, press test again and now your meter will read 0.00 Mohm.
Now that error has been removed you can remove the link cable.

## Slide 6
Step 4: At the consumer unit identify the circuit you want to test.
Connect the link cable between the live cable and earth

## Slide 7
Step 5: At the light switch or ceiling rose connect the negative to the earth cable and red connector to the live.(switched live ) Note the reading
Live

## Slide 8
Step 6: Turn the light switch off and the reading should change. Ideally if this is a new install the reading will be infinity , on this meter its showing 999 as this is the maximum range.
Note down the reading.
You have proven
Polairty.
Step7 : At consumer unit remove the link cable and reinstate the live. Same test can be done on next circuit

## Slide 9
Purpose​
To ensure the insulation resistance of each conductor is of an acceptable value and there are no short circuits. Proving the insulation is sufficient.​
Equipment​
Insulation resistance test meter​
Setting​
Test voltage dependant on circuit nominal voltage. For nominal voltage of up to and including 500 volts a test voltage of 500 volts is applied.​
Measured in
- MegaOhms MΩ
Insulation Resistance Testing

## Slide 10
Step 1: Remove all loads and switch off all the breakers including RCD’s
Step 2: Insert the cabels into Green and red terminals

## Slide 11
Step 3: Turn the meter to 500VDC. This is the test voltage for 220 and 440 systems
Step4: Connect the leads together and press test. This will test the leads- a 0.00 shows leads are shorted together with no breaks.

## Slide 12
Step 5: At the consumer unit connect 1 lead to earth and 1 into live
Note the results

## Slide 13
Step 6: Now connect the Live to neutral: Record Your Results

## Slide 14
Step 7: Now connect the Earth to neutral: Record Your Results:

## Slide 15: IR Results
Red Lead | Green Lead | Results
Live | Neutral | 
Live | Earth | 
Earth | Neutral | 
The acceptable value is 1MOhm, however 2 MOhm should be investigated. For new installation we accept a very high IR reading.