## Slide 1: Safe Isolation Overview
Isolation

## Slide 2: Safe Isolation and locking-off procedure

## Slide 3: EAWR Regulation 12.
Regulation 12 requires that a suitable means of isolation:
“have the capability to positively establish an air gap which will ensure that there is no likely way in which the isolation gap can fail electrically”.

## Slide 4: IET Wiring Regulations (BS7671)
Switching off for mechanical maintenance
Regulation 537.3.1.2 – suitable means shall be provided to prevent electrically powered equipment from becoming unintentionally reactivated during the mechanical maintenance, unless the means of switching off is continuously under the control of any person performing such maintenance.

## Slide 5: Lock out Procedure
Why do we need a lock out procedure?
To keep plant and its components from being set in motion
To prevent release of stored energy
To protect safety of persons

## Slide 7: Lock Out Devices
​​

## Slide 8: Lock Out Devices

## Slide 9: Lockout Tag
On the system isolated a tag must be included with the safety lock.

## Slide 10: Safe Isolation and locking-off procedure
Agree the work to be carried out and circuit/equipment to be isolated.
Carry out a procedure for assessment if the circuit can be made ‘dead’ in a safe manner.
Activate a ‘permit-to-work’ system if required.
Identify the circuit/equipment to be isolated.
Verify the operation of test equipment using a known live source.
Determine the operational status of the circuit/equipment to be isolated.
Notify all relevant personnel that isolation is about to take place.
Identify the relevant means of isolation.

## Slide 11
9 Switch off and lock-off the means of isolation.
10 Post ‘danger’ and ‘caution’ notices.
11 Retain lock-off key/s in a secure place.
12 Use proven test instruments to verify that all sources of energy have been removed from the circuit/equipment.
(NOTE: work on the circuit/equipment should not commence until isolation is verified.)
13 Apply safety earths if required (this is always required for HV systems).
14 Apply safety locks and caution notices to earthing devices.
15 Issue permit-to-work.