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FEATURES

(1) Small monitoring current of 45 u A

(2) 2-wire system

(3) Alarm response lamp (LED)

(4) Simple mounting

(5) Very easy maintenance

(6) Very low profile

(7) Conventional type

(8) Approved by Japan Fire Equipment Inspection Institute

DESCRIPTION

The FDK series photoelectric smoke detectors detect
combustion products (smoke) generated by a fire, and
transmit an alarm signal to the fire alarm control panel.
The photoelectric smoke detector can deteot a fire in an
earlier stage than a heat detector. Generally, this
detector is installed in the spaces such as basements,
ordinary fioors, corridors, staircases, elevator shafts.

OPERATING PRINCIPLE AND FUNCTION WITH RECESS MOUNTING BASE
The photoelectric smoke detector is composed of a light
source, light sensing element, light shielding element
and detecting chamber. The light source (a
light-emitting diode) emits light at intervals of about 3.5
seconds, which does not reach the light sensing
element (photo diode) under normal conditions because
of the light shielding mold. If smoke enters the detecting
cchamber, the light from the light source is scattered by
smoke particles and reaches the light sensing element
The light reaching the light sensing element varies with
'smoke density and if it exceeds the predetermined level,
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